ACOUSTIC CEILING HANGERS (SPRING)

Update blue text to suit project

  - Description

- Scope

- All cinema auditoria ceilings shall suspended from helical acoustic ceiling hangers to prevent the transmission of sound and vibration to the building structure. Use ceiling hangers supplied by Mason U.K. Ltd or equal and approved.

Mason UK Ltd: Tel 01252 716610 or www.mason-uk.co.uk.

- All isolation materials shall be supplied by the same manufacturer.

- Any variance or non-compliance with the specification shall be corrected by the contractor in an approved manner.

  - Submittal data requirements

A.  The manufacturer of the vibration isolation shall provide submittals for products as follows:

- Catalogue data sheets.

- Specifications of hangers, to include deflection range, load range and calculated deflection and natural frequency based on specific ceiling load.

- Tested failure load of hanger box to demonstrate integrity and safety of design.

Specification

- The helical spring element shall be selected to have a deflection of between 15mm-20mm. When loaded, the hanger natural frequency shall not exceed 5Hz.

- The spring is to sit in a rubber cup located in the hanger box by a moulded rubber lip to prevent the connecting rod touching the hanger box, causing a vibration short-circuit. The design of the hanger shall allow the top hanger rod to swing through an arc of 30o.

- Hanger boxes shall be manufactured of minimum 2mm thick box section steel and powder coated to prevent corrosion.

- Springs shall have a minimum additional travel to solid equal to 50% of the specified static deflection.

- The spring diameter shall be not less than 80% of the compressed height at rated load.

- The hangers shall feature a profiled hook to allow the hanger to clip directly onto the British Gypsum MF7 primary channel.

- Hangers shall be HDQF-X as manufactured by Mason Industries or equivalent.