- FORMWORK CONCRETE FLOOR SYSTEM

- Update blue text to suit project

1.01 Description

- A. Scope of Work

Isolate the recording studio floor(s) from the building structure with a formwork floating floor using special compound Low Dynamic Stiffness (LDS) rubber isolators by Mason UK Ltd or equal or approved, reinforced concrete and perimeter isolation.

- Mason UK Ltd: Tel 01252 716610 or www.mason-uk.co.uk.

1.02 Design

- A. Intent

1.	The recording studio floating floor(s) shall consist of a 100mm thick dense reinforced concrete slab on 18mm WPB plywood isolated from and supported not less than 50mm above the structural slab by resilient LDS rubber isolators.

2.	The floating floor slab shall be isolated from main structure, adjoining walls and curbs by means of 25mm perimeter isolation board.

- B. Performance Requirements

1.	LDS isolators shall have the minimum deflection to obtain the design natural frequency of between

8Hz-12Hz at the design dead load condition to comply with the acoustic specification.

2.	The floating floor design shall include all structural requirements to meet the design dead load of 1.8 -3.6kN/m2 (depending on floor thickness) plus 5.0kN/m2 for seating and or floor finishes etc. and a live load of 5kN/m2 (to be confirmed by the structural engineer)

- C. Floor System Construction Procedure

1.	Cement perimeter isolation board around all walls, columns, curbs, etc.

2.	Lay 50mm mineral wool on the structural floor.

3.	Mark out on the floor as per the isolator manufacturer’s design drawing and place isolators at each location.

4.	Lay sheets of 18mm WPB plywood on the isolators so that half of the isolator projects out to support the next plywood sheet around the sides and at the corners. The plywood joints shall be staggered. Connect each plywood sheet to the adjacent sheets with junction plates.

5.	Cover entire floor area with 125micron polythene sheeting and carry sheeting over the perimeter isolation board and 400mm up walls.

6.	Place and fix the steel reinforcing as shown on the design and installation drawing and pour the concrete monolithically.

7.	The floor will have a power float finish.

- D. Submittals

1.	Detailed product drawings including upon request load, deflection and indicative dynamic response curves of all isolators, verified by an independent source.

2.	Drawings to show:

a.	Dead, live and concentrated loads.

b.	Isolator sizes, deflections and locations.

c.	Size, type, elevation and spacing of concrete reinforcement.

d.	Floating floor construction procedure.

1.03 Quality Assurance

- A. Requirements

1. 	Floating floor system components shall be designed and fabricated by a manufacturer with at least five years experience and with at least thirty or more similar installations.

2. 	The floating floor shall be designed by the isolator manufacturer.

3. 	The design and installation shall be covered by professional indemnity insurance.

1.04 Site Conditions

1.	If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-floor must have the same pitch as the top of the floating floor and have a smooth trowel finish with no ridge or depressions and with a tolerance of +/- 5mm over 5m and no greater deviation than 20mm over the entire floor area.

1.05 Sequencing and Scheduling

1.	Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

- PART 2 - PRODUCTS

- 2.01 Isolators

1.	50mm thick isolator moulded to the following AASHTO Bridge Bearing specification as in Table 1.  The isolators shall be Mason Industries type EAFM or equal or approved.

| PHYSICAL PROPERTIES |  |  | TESTING FOR AGING |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | HEAT RESISTANCE (70h/70°C) |  |  | OZONE | COMPRESSION SET |
| Tests: ASTM D-2240 and D-412 |  |  | ASTM D-573 |  |  | ASTM D-1149 | ASTM D-395 |
| Hardness (Shore A Durometer) | Tensile Strength (min) | Elongation at Break (min) | Hardness Change (max) | Tensile Strength Change (max) | Elongation at Break Change (max) | 25 pphm in air by volume 20% strain 400C | 22 hours 700 C (max creep) |
| 50 +/- 5 60 +/- 5 70 +/- 5 | 2250 psi 2250 psi 2250 psi | 450% 400% 300% | 10% 10% 10% | -25% -25% -25% | -25% -25% -25% | No Cracks No Cracks No Cracks | 25% 25% 25% |

Table 1. AASHTO Bridge Bearing Natural Rubber Specifications

- 2.02 Plywood

- 1.	Provide one layer 18mm WPB plywood and adjoining plates.

- 2.03 Polythene Material

- 1.	Provide one layer of 125micron polyethylene sheeting.

- 2.04 Perimeter Isolation Board

1.	Rockwool isolation board, 25mm thick and density of 100kg/m3.