FORMWORK WOODEN FLOOR SYSTEM

USING PAVING SLABS

Update blue text to suit project

1.01 Description

A. Scope of Work

Isolate the studio floor(s) from the building structure with a formwork floating floor using Low Dynamic Stiffness (LDS) rubber isolators by Mason UK Ltd or equal or approved, supporting wooden boards sandwiching concrete paving slabs.

Mason UK Ltd: Tel 01252 716610 or www.mason-uk.co.uk.

1.02 Design

A. Intent

1.	The studio floating floor(s) shall consist of a xx mm thick floor constructed from 2 layer of 12mm WPB plywood / cement particle board, 50mm thick concrete paving slabs (council slabs) and a top layer of 18mm WPB plywood / cement particle board isolated from and supported not less than 50mm above the structural slab by resilient LDS rubber isolators.

2.	The floating floor shall be isolated from main structure with a 50mm gap filled with low density mineral fibre insulation and from adjoining walls and curbs by means of  25 mm mineral fibre perimeter isolation board of 100kg/m3 density.

B. Performance Requirements

1.	Natural rubber isolators shall have the minimum deflection to obtain the design natural frequency of between

8Hz-12Hz at the design dead load condition to comply with the acoustic specification.

2.	The floating floor design shall include all structural requirements to meet the design dead load of xxkN/m2 (depending on floor thickness and seating loads and floor finishes) and a live load of 5kN/m2 (to be confirmed by the structural engineer)

C. Floor System Construction Procedure

1.	Cement 25mm perimeter isolation board around all walls, columns, curbs, etc.

2.	Lay 50 mm mineral wool on the structural floor.

3.	Mark out the isolator locations on the mineral wool as per the isolator manufacturer’s design drawing,  Holes to be cut of suitable diameter through the mineral fibre and isolators of correct type to be inserted at each location.

4.	Shim each isolator so maximum deviation is +/- 2mm between adjacent mounts

4.	Lay 2 layers of 12mm WPB plywood on the isolators over entire room carefully cutting plywood to size where necessary. The plywood sheets shall be staggered to avoid coinciding joints.  Boards to be screwed together with appropriate wood screws. Paving slabs to be placed onto plywood and fixed with suitable adhesive.  Paving slabs to be butted together. A top layer of 18mm WPB plywood / cement particle board to be placed over paving slabs with a suitable adhesive. Whole assembly to be held together with wood screws passing through the paving slabs to the bottom boards. Minimum 400mm o/c.  Screws must not touch the rubber isolators.

5.	The floor is now ready for further finishes.

D. Submittals

1.	Detailed product drawings including upon request load, deflection and indicative dynamic response curves of all isolators.

2.	Drawings to show:

a.	Dead, live and concentrated loads.

b.	Isolator sizes, deflections and locations.

c.	Size, type, and elevation of all floor layers.

d.	Floating floor construction procedure.

1.03 Quality Assurance

A. Requirements

1. 	Floating floor system components shall be designed by a manufacturer with at least five years experience and with at least thirty or more similar installations.

2. 	The floating floor shall be designed by the isolator manufacturer.

3. 	The design and installation shall be covered by professional indemnity insurance.

1.04 Site Conditions

1.	If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-floor must have the same pitch as the top of the floating floor and have a smooth trowel finish with no ridges or depressions and with a tolerance of +/- 5mm over 5m and no greater deviation than 20mm over the entire floor area.

1.05 Sequencing and Scheduling

1.	Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PART 2 - PRODUCTS

2.01 Isolators

1.	50mm thick isolator moulded to the following AASHTO Bridge Bearing specification as in Table 1.  The isolators shall be Mason Industries type EAFM or equal or approved.

| PHYSICAL PROPERTIES |  |  | TESTING FOR AGING |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | HEAT RESISTANCE (70h/70°C) |  |  | OZONE | COMPRESSION SET |
| Tests: ASTM D-2240 and D-412 |  |  | ASTM D-573 |  |  | ASTM D-1149 | ASTM D-395 |
| Hardness (Shore A Durometer) | Tensile Strength (min) | Elongation at Break (min) | Hardness Change (max) | Tensile Strength Change (max) | Elongation at Break Change (max) | 25 pphm in air by volume 20% strain 400C | 22 hours 700 C (max creep) |
| 50 +/- 5 60 +/- 5 70 +/- 5 | 2250 psi 2250 psi 2250 psi | 450% 400% 300% | 10% 10% 10% | -25% -25% -25% | -25% -25% -25% | No Cracks No Cracks No Cracks | 25% 25% 25% |

Table 1. AASHTO Bridge Bearing Natural Rubber Specifications

2.02 Plywood

1.	Provide 2 layers of 12mm WPB plywood bottom layer and 18mm WPB plywood top layer.