FORMWORK WOODEN FLOOR SYSTEM SUPPORTED BY SPRINGS

Update blue text to suit project

1.01 Description

A. Scope of Work

Isolate the gymnasium floor(s) from the building structure with a lightweight floating floor construction using spring isolators by Mason UK Ltd or equal or approved supporting multiple flooring layers and perimeter isolation.

Mason UK Ltd: Tel 01252 716610 or www.mason-uk.co.uk.

1.02 Design

A. Intent

1.	The gymnasium floating floor(s) shall consist of a floor constructed from No. board layers of 18mm WPB plywood / cement particle board isolated from and supported above the structural slab by isolators incorporating a metal spring. 50mm section joists are to be used between the isolators and the flooring layers.

2.	The floating floor slab shall be isolated from main structure, adjoining walls and curbs by means of 10mm perimeter isolation board.

B. Performance Requirements

1.	Isolators shall of a spring type and have the minimum deflection to obtain the design natural frequency of between 5Hz-8Hz at the design dead load condition to comply with the acoustic specification.

2.	The floating floor design shall include all structural requirements to meet the design dead load of xxxkN/m2  and a live load of 5kN/m2 (to be confirmed by the structural engineer)

C. Floor System Construction Procedure

1.	Cement perimeter isolation board around all walls, columns, curbs, etc.

2.	Lay 50mm mineral wool on the structural floor between the isolator rows if required.

3.	Mark out on the floor as per the isolator manufacturer’s design drawing and place isolators at each location.

4.	Attach wooden joists on top of the isolators and place so they run in parallel lines across the entire area.

5.	Lay a sheet of 18mm WPB plywood on the joists so they are fully supported around the edges and at the corners. The plywood joints shall be staggered. Subsequent layers of board shall also be staggered both horizontally and vertically relative to lower layers. Layers are to be bonded and screwed together, taking care not to screw through isolators.

6.	The floor is now ready for further finishes.

D. Submittals

1.	Detailed product drawings including upon request load, deflection and indicative dynamic response frequencies of the isolators.

2.	Drawings to show:

a.	Dead, live and concentrated loads.

b.	Isolator sizes, deflections and locations.

c.	Size, type, elevation and placing of joists and all floor layers.

d.	Floating floor construction procedure.

1.03 Quality Assurance

A. Requirements

1. 	Floating floor system components shall be designed and fabricated by a manufacturer with at least five years experience and with at least thirty or more similar installations.

2. 	The floating floor shall be designed by the isolator manufacturer.

3. 	The design and installation shall be covered by professional indemnity insurance.

1.04 Site Conditions

1.	If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolation manufacturer. The sub-floor must have the same pitch as the top of the floating floor and have a smooth trowel finish with no ridge or depressions and with a tolerance of +/- 5mm over 5m and no greater deviation than 20mm over the entire floor area.

1.05 Sequencing and Scheduling

1.	Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PART 2 - PRODUCTS

2.01 Isolators

1.	Helical spring welded to a minimum 16 gauge electro plated steel plate and fitted into a non skid neoprene acoustic cup. The spring is to be electro plated against corrosion. The springs shall have an additional travel to solid equal to 50% over rated maximum deflection. The spring diameters shall be not less than 80% of the compressed height at the rated load.

2.	Spring isolators to be MFS manufactured by Mason U.K. or equivalent.

2.02 Boards

1.	Provide XXno. layers of 18mm WPB plywood/ cement particle board and adjoining plates.

2.03 Perimeter Isolation Board

1.	Closed cell Neoprene foam board, 10mm thick and density of 120kg/m3.