JACK-UP CONCRETE FLOOR SYSTEM - SPRING

Update blue text to suit project

1.01 Description

A. Scope of Work

Isolate the Gym Floor from the building structure with a jack-up floating floor using spring isolators by Mason UK Ltd or equal or approved.

Mason UK Ltd: Tel 01252 716610 or www.mason-uk.co.uk.

1.02 Design

A. Intent

1.	The Gym floating floor(s) shall consist of a 150mm thick dense reinforced concrete slab isolated from and supported not less than 60mm above the structural slab by helical spring isolators within cast iron housings designed to jack or lift the floor.

2.	The floating floor slab shall be isolated from main structure, adjoining walls and curbs by means of 25mm perimeter isolation board.

B. Performance Requirements

1.	Helical spring shall have the minimum deflection to obtain the design natural frequency of between

3Hz-4Hz at the design dead load condition to comply with the acoustic specification.

2.	The floating floor design shall include all structural requirements to meet the design dead load of 3.0kN/m2 (depending on floor thickness) plus 0.5kN/m2 for equipment and floor finishes etc. and a live load of up to 5kN/m2.

C. Floor System Construction Procedure

1.	The setting of all isolation materials and raising of the floor shall be performed or supervised by the isolation manufacturer and should not be sub-contracted.

2.	Fix perimeter isolation board around all walls, columns, curbs, etc.

3.	Cover entire floor area with 125micron polyethylene sheeting and carry sheeting over the perimeter isolation board and 500mm up walls.

4.	Mark out on the floor as per the manufacturer’s design drawing and place isolator castings at each location.

5.	Place and fix the steel reinforcing as shown on the design and installation drawing and pour the concrete monolithically.

6.	The floor will have a skip float / power float finish.

7.	Raise floor not less than 60mm. The minimum air gap must not be compromised by the deflection of the isolator.

D. Submittals

1.	Detailed product drawings including load, deflection and dynamic response curves of all isolators.

2.	Drawings to show:

a.	Dead, live and concentrated loads.

b.	Isolator sizes, deflections, natural frequencies and locations.

c.	Size, type, elevation and spacing of concrete reinforcement.

d.	Caulking details.

e.	Floating floor construction procedure.

1.03 Quality Assurance

A. Requirements

1.	Floating floor system components shall be designed and fabricated by a manufacturer with at least five years experience.

2.	The floating floor shall be designed, installed and raised by the isolator manufacturer or approved partner.

3.	The design and installation shall be covered by professional indemnity insurance.

1.04 Site Conditions

1.	If site conditions are unsatisfactory or raise questions about the installation of the floating floor, the work will not proceed until the condition has been corrected in a manner acceptable to the isolator manufacturer. The sub-floor must have the same pitch as the top of the floating floor and have a smooth trowel finish with no ridge or depressions and with a tolerance of +/- 5mm over 5m and no greater deviation than 20mm over the entire floor area.

1.05 Sequencing and Scheduling

1.	Coordinate work with other trades and coordinate scheduling with the construction supervisor to minimize delays.

PART 2 - PRODUCTS

2.01 Isolators

1.	Bell shaped castings with integral lugs to locate reinforcing steel, shrouding helical spring, integral steel compression housing and top plate. All springs are to be powder coated against corrosion. The springs shall have an additional travel to solid equal to 50% over rated maximum deflection. The spring diameters shall be not less than 80% of the compressed height at the rated load.

2.	The isolators shall be Mason Industries type FS or equal or approved.

2.02 Bond Break Material

1.	Provide one layer of 150micron polyethylene sheeting.

2.03 Perimeter Isolation Board

1.	Rockwool isolation board, 25mm thick and density of 100kg/m3.